## HEATING
Description | code | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
none | SUPPLY_HEATING_AS0 | NONE | NONE | 0 | 0 | 20 | 1 | 5 | educated guess
oil-fired boiler - Konstanttemperaturkessel - 10 kW | SUPPLY_HEATING_AS1 | OIL | BUILDING | 0.7 | 1560.1736 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Konstanttemperaturkessel - 50 kW | SUPPLY_HEATING_AS2 | OIL | BUILDING | 0.7 | 383.6218 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Konstanttemperaturkessel - 100 kW | SUPPLY_HEATING_AS3 | OIL | BUILDING | 0.7 | 277.3312 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 10 kW | SUPPLY_HEATING_AS4 | OIL | BUILDING | 0.85 | 1284.8489 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 50 kW | SUPPLY_HEATING_AS5 | OIL | BUILDING | 0.85 | 315.9238 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 100 kW | SUPPLY_HEATING_AS6 | OIL | BUILDING | 0.85 | 228.3904 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 10 kW | SUPPLY_HEATING_AS7 | OIL | BUILDING | 0.92 | 1187.0886 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 50 kW | SUPPLY_HEATING_AS8 | OIL | BUILDING | 0.93 | 288.7476 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 100 kW | SUPPLY_HEATING_AS9 | OIL | BUILDING | 0.93 | 208.7439 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 10 kW | SUPPLY_HEATING_AS10 | NATURALGAS | BUILDING | 0.7 | 771.1885 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 50 kW | SUPPLY_HEATING_AS11 | NATURALGAS | BUILDING | 0.7 | 217.5196 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 100 kW | SUPPLY_HEATING_AS12 | NATURALGAS | BUILDING | 0.7 | 192.7971 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 10 kW | SUPPLY_HEATING_AS13 | NATURALGAS | BUILDING | 0.85 | 635.0964 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 50 kW | SUPPLY_HEATING_AS14 | NATURALGAS | BUILDING | 0.85 | 179.1338 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 100 kW | SUPPLY_HEATING_AS15 | NATURALGAS | BUILDING | 0.85 | 158.7741 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Brennwertgerät - 10 kW | SUPPLY_HEATING_AS16 | NATURALGAS | BUILDING | 0.93 | 580.4644 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas- boiler - Brennwertgerät - 50 kW | SUPPLY_HEATING_AS17 | NATURALGAS | BUILDING | 0.95 | 160.2776 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Brennwertgerät - 100 kW | SUPPLY_HEATING_AS18 | NATURALGAS | BUILDING | 0.95 | 142.061 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
biomass boiler - 10 kW | SUPPLY_HEATING_AS19 | WETBIOMASS | BUILDING | 0.9 | 1208.8544 | 20 | 6 | 5 | KEA Technikatalog
biomass boiler - 50 kW | SUPPLY_HEATING_AS20 | WETBIOMASS | BUILDING | 0.81 | 597.25 | 20 | 6 | 5 | KEA Technikatalog
biomass boiler - 100 kW | SUPPLY_HEATING_AS21 | WETBIOMASS | BUILDING | 0.81 | 416.0371 | 20 | 6 | 5 | KEA Technikatalog
heatpump soil/water - 10 kW | SUPPLY_HEATING_AS22 | GRID | BUILDING | 4.25 | 845.332 | 20 | 0.58005 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump soil/water - 50 kW | SUPPLY_HEATING_AS23 | GRID | BUILDING | 4.25 | 520.7323 | 20 | 0.94162 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump soil/water - 100 kW | SUPPLY_HEATING_AS24 | GRID | BUILDING | 4.25 | 324.5996 | 20 | 1.5106 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 10 kW | SUPPLY_HEATING_AS25 | GRID | BUILDING | 3.6 | 554.1657 | 20 | 1.1838 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 50 kW | SUPPLY_HEATING_AS26 | GRID | BUILDING | 3.6 | 341.5297 | 20 | 1.9209 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 100 kW | SUPPLY_HEATING_AS27 | GRID | BUILDING | 3.6 | 212.8946 | 20 | 3.0816 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump - air/air | SUPPLY_HEATING_AS28 | GRID | BUILDING | 2.7 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
heatpump - water/water | SUPPLY_HEATING_AS29 | GRID | BUILDING | 3 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
coal-fired furnace | SUPPLY_HEATING_AS30 | COAL | BUILDING | 0.6 | 367 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, Connolly et al. (2013). Costs in the EU boiler <25 kW)
electrical boiler | SUPPLY_HEATING_AS31 | GRID | BUILDING | 0.9 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required
wood-furnace | SUPPLY_HEATING_AS32 | WOOD | BUILDING | 0.6 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required
district heating - natural gas-fired boiler | SUPPLY_HEATING_AS33 | NATURALGAS | DISTRICT | 0.6 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
district heating - heatpump - soil/water | SUPPLY_HEATING_AS34 | GRID | DISTRICT | 0.6 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
district heating - heat pump - water/water | SUPPLY_HEATING_AS35 | GRID | DISTRICT | 2.7 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
Note on A33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All values + 15% of vertailverluste not included in th original factors. In order to trasnform from useful to final energy

## HOT_WATER
Description | code | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
none | SUPPLY_HOTWATER_AS0 | NONE | NONE | 0 | 0 | 20 | 1 | 5 | educated guess
oil-fired boiler - Konstanttemperaturkessel - 10 kW | SUPPLY_HOTWATER_AS1 | OIL | BUILDING | 0.7 | 1560.1736 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Konstanttemperaturkessel - 50 kW | SUPPLY_HOTWATER_AS2 | OIL | BUILDING | 0.7 | 383.6218 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Konstanttemperaturkessel - 100 kW | SUPPLY_HOTWATER_AS3 | OIL | BUILDING | 0.7 | 277.3312 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 10 kW | SUPPLY_HOTWATER_AS4 | OIL | BUILDING | 0.85 | 1284.8489 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 50 kW | SUPPLY_HOTWATER_AS5 | OIL | BUILDING | 0.85 | 315.9238 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Niedertemperaturkessel - 100 kW | SUPPLY_HOTWATER_AS6 | OIL | BUILDING | 0.85 | 228.3904 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 10 kW | SUPPLY_HOTWATER_AS7 | OIL | BUILDING | 0.92 | 1187.0886 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 50 kW | SUPPLY_HOTWATER_AS8 | OIL | BUILDING | 0.93 | 288.7476 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
oil-fired boiler - Brennwertgerät - 100 kW | SUPPLY_HOTWATER_AS9 | OIL | BUILDING | 0.93 | 208.7439 | 20 | 3.5 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 10 kW | SUPPLY_HOTWATER_AS10 | NATURALGAS | BUILDING | 0.7 | 771.1885 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 50 kW | SUPPLY_HOTWATER_AS11 | NATURALGAS | BUILDING | 0.7 | 217.5196 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Konstanttemperaturkessel - 100 kW | SUPPLY_HOTWATER_AS12 | NATURALGAS | BUILDING | 0.7 | 192.7971 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 10 kW | SUPPLY_HOTWATER_AS13 | NATURALGAS | BUILDING | 0.85 | 635.0964 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 50 kW | SUPPLY_HOTWATER_AS14 | NATURALGAS | BUILDING | 0.85 | 179.1338 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Niedertemperaturkessel - 100 kW | SUPPLY_HOTWATER_AS15 | NATURALGAS | BUILDING | 0.85 | 158.7741 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Brennwertgerät - 10 kW | SUPPLY_HOTWATER_AS16 | NATURALGAS | BUILDING | 0.93 | 580.4644 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas- boiler - Brennwertgerät - 50 kW | SUPPLY_HOTWATER_AS17 | NATURALGAS | BUILDING | 0.95 | 160.2776 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
natural gas-fired boiler - Brennwertgerät - 100 kW | SUPPLY_HOTWATER_AS18 | NATURALGAS | BUILDING | 0.95 | 142.061 | 20 | 3 | 5 | https://www.effizienzhaus-online.de/lexikon/wirkungsgrad/, KEA Technikkatalog
biomass boiler - 10 kW | SUPPLY_HOTWATER_AS19 | WETBIOMASS | BUILDING | 0.9 | 1208.8544 | 20 | 6 | 5 | KEA Technikatalog
biomass boiler - 50 kW | SUPPLY_HOTWATER_AS20 | WETBIOMASS | BUILDING | 0.81 | 597.25 | 20 | 6 | 5 | KEA Technikatalog
biomass boiler - 100 kW | SUPPLY_HOTWATER_AS21 | WETBIOMASS | BUILDING | 0.81 | 416.0371 | 20 | 6 | 5 | KEA Technikatalog
heatpump soil/water - 10 kW | SUPPLY_HOTWATER_AS22 | GRID | BUILDING | 4.25 | 845.332 | 20 | 0.58005 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump soil/water - 50 kW | SUPPLY_HOTWATER_AS23 | GRID | BUILDING | 4.25 | 520.7323 | 20 | 0.94162 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump soil/water - 100 kW | SUPPLY_HOTWATER_AS24 | GRID | BUILDING | 4.25 | 324.5996 | 20 | 1.5106 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 10 kW | SUPPLY_HOTWATER_AS25 | GRID | BUILDING | 3.6 | 554.1657 | 20 | 1.1838 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 50 kW | SUPPLY_HOTWATER_AS26 | GRID | BUILDING | 3.6 | 341.5297 | 20 | 1.9209 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump air/water - 100 kW | SUPPLY_HOTWATER_AS27 | GRID | BUILDING | 3.6 | 212.8946 | 20 | 3.0816 | 5 | Technologiesteckbriefe: https://energy.ec.europa.eu/system/files/2021-01/de_ca_2020_de_0.pdf
heatpump - air/air | SUPPLY_HOTWATER_AS28 | GRID | BUILDING | 2.7 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
heatpump - water/water | SUPPLY_HOTWATER_AS29 | GRID | BUILDING | 3 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
coal-fired furnace | SUPPLY_HOTWATER_AS30 | COAL | BUILDING | 0.6 | 367 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, Connolly et al. (2013). Costs in the EU boiler <25 kW)
electrical boiler | SUPPLY_HOTWATER_AS31 | GRID | BUILDING | 0.9 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required
wood-furnace | SUPPLY_HOTWATER_AS32 | WOOD | BUILDING | 0.6 | 200 | 20 | 1 | 5 | from CEA Switzerland, adjustments required
district heating - natural gas-fired boiler | SUPPLY_HOTWATER_AS33 | NATURALGAS | DISTRICT | 0.6 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
district heating - heatpump - soil/water | SUPPLY_HOTWATER_AS34 | GRID | DISTRICT | 0.6 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
district heating - heat pump - water/water | SUPPLY_HOTWATER_AS35 | GRID | DISTRICT | 2.7 | 100 | 20 | 1 | 5 | from CEA Switzerland, adjustments required, educated guess
Note on A33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All values + 15% of vertailverluste not included in th original factors. In order to trasnform from useful to final energy

## COOLING
Description | code | system | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
none | SUPPLY_COOLING_AS0 | NONE | NONE | NONE | 0 | 0 | 20 | 1 | 5 | educated guess
heatpump - air/air | SUPPLY_COOLING_AS1 | COOLING | GRID | BUILDING | 2.7 | 200 | 20 | 1 | 5 | educated guess
heatpump - water/water | SUPPLY_COOLING_AS2 | COOLING | GRID | BUILDING | 3 | 200 | 20 | 1 | 5 | educated guess
district cooling - Lakewater/water | SUPPLY_COOLING_AS3 | COOLING | GRID | DISTRICT | 3.2 | 200 | 20 | 1 | 5 | educated guess
district cooling - air/air | SUPPLY_COOLING_AS4 | COOLING | GRID | DISTRICT | 2.8 | 200 | 20 | 1 | 5 | educated guess

## ELECTRICITY
Description | code | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
none | SUPPLY_ELECTRICITY_AS0 | NONE | NONE | 0 | 0 | 20 | 1 | 5 | educated guess
Swiss consumer energy mix | SUPPLY_ELECTRICITY_AS1 | GRID | CITY | 0.99 | 1 | 20 | 1 | 5 | educated guess
German consumer energy mix | SUPPLY_ELECTRICITY_AS2 | GRID | CITY | 0.94 | 1 | 20 | 1 | 5 | Statistisches Bundesamt 2019 Monatsbericht über die Elektrizitätsversorgung