## photovoltaic_panels
Description | code | type | cap_min | cap_max | unit | module_length_m | PV_th | PV_n | PV_noct | V_power_supply | PV_Bref | PV_a0 | PV_a1 | PV_a2 | PV_a3 | PV_a4 | misc_losses | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic monocrystalline panel | PV1 | PV | 1 | 10000 | W | 1 | 0.002 | 0.16 | 43.5 | 30 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.16 | 43.5 | 30 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.16 | 43.5 | 30 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic polycrystalline panel | PV2 | PV | 1 | 10000 | W | 1 | 0.002 | 0.15 | 43.9 | 30 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.15 | 43.9 | 30 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.15 | 43.9 | 30 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic amorphous silicon panel | PV3 | PV | 1 | 10000 | W | 1 | 0.002 | 0.08 | 38.1 | 30 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.08 | 38.1 | 30 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.08 | 38.1 | 30 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity

## solar_thermal_panels
Description | code | type | module_length_m | module_area_m2 | aperture_area_ratio | n0 | c1 | c2 | mB0_r | mB_max_r | mB_min_r | C_eff | T_supply_sup | t_max | IAM_d | dP1 | dP2 | dP3 | dP4 | Cp_fluid | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
flat plate | SC1 | FP | 2 | 2.023 | 0.888 | 0.775 | 3.91 | 0.0081 | 57.98 | 86.97 | 28.99 | 8000 | 60 | 192 | 0.87 | 0 | 94.6324 | 150.2986 | 44.5329 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2.131 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%
evacuated tube | SC2 | ET | 2 | 4.322 | 0.655 | 0.721 | 0.89 | 0.0199 | 88.2 | 147.12 | 33.1 | 39000 | 100 | 196 | 0.91 | 0 | 2825.9464 | 7771.3527 | 706.4866 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2.131 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%

## photovoltaic_thermal_panels
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic PVT | PVT1 | 1 | 10000000000 | W | USD-2015 | 0 | 5.1975 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%

## unitary_air_conditioners
Description | code | type | cap_min | cap_max | unit | rated_COP_seasonal | V_power_supply | T_air_indoor_rating | T_air_outdoor_rating | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
air conditioner, split-system, air cooled | AC1 | mini-split | 0 | 19000 | W | 3.7 | 230 | 27 | 35 | USD-2015 | 0 | 1.6 | 1 | 0 | 0 | 25 | 5 | 5 | all | ASHRAE 90.1/2019 - minimum efficiency rating, AHRI 210/240 (2023) temperature rating - application rating conditions
air conditioner, split-system, air cooled, ducted | AC2 | mini-split, ducted | 0 | 19000 | W | 3.5 | 230 | 27 | 35 | USD-2015 | 0 | 1.6 | 1 | 0 | 0 | 25 | 5 | 5 | all | ASHRAE 90.1/2019 - minimum efficiency rating, AHRI 210/240 (2023) temperature rating - application rating conditions

## vapor_compression_chillers
Description | code | type | cap_min | cap_max | unit | min_eff_rating | V_power_supply | T_cond_design | T_evap_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
electrically operated centrifugal, water cooled | CH1 | water-centrifugal | 1050000 | 70000000 | W | 6.3 | 380 | 34.61 | 6.67 | USD-2015 | 1568000 | 0.3049 | 1 | 0 | 0 | 25 | 5 | 5 | Fit based on RESCUE WP 2.4. Figure 18 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | water-reciprocating | 1 | 260000 | W | 4.7 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | water-reciprocating | 260000 | 530000 | W | 4.9 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | water-reciprocating | 530000 | 1050000 | W | 5.3 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | water-reciprocating | 1050000 | 2110000 | W | 5.8 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | water-reciprocating | 2110000 | 70000000 | W | 6.3 | 380 | 34.61 | 6.67 | USD-2015 | 0 | 0.36063 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load

## absorption_chillers
Description | code | type | cap_min | cap_max | unit | min_eff_rating | aux_power | V_power_supply | T_gen_design | T_cond_design | T_evap_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | s_e | r_e | s_g | r_g | a_e | e_e | a_g | e_g | m_cw | m_hw | reference
LiBr single effect - indirect | ACH1 | single | 0 | 51150 | W | 0.7 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr single effect - indirect | ACH1 | single | 51150 | 1176000 | W | 0.7 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 68.12 | -3281.1 | 88.05 | -4216.1 | -1.45 | 1.75 | -1.45 | 1.75 | 81 | 33 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr double effect (dummy) - indirect | ACH2 | double | 0 | 58150 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr double effect - indirect | ACH2 | double | 58150 | 1337450 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr double effect - indirect | ACH2 | double | 1337450 | 10000000000 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr triple effect - indirect | ACH3 | triple | 116300 | 1628200 | W | 1.2 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.6424 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 14.6 | -1171.7 | 7.05 | -504.2 | -2.14 | 3.29 | -2.14 | 3.29 | 62 | 10

## cooling_towers
Description | code | type | cap_min | cap_max | unit | aux_power | V_power_supply | T_water_in_design | T_water_out_design | T_air_in_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
centralized cooling tower | CT1 | open-circuit | 1 | 10000000 | W | 1.26% | 460 | 35 | 29.5 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 10 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT1 | open-circuit | 10000000 | 10000000000000000 | W | 1.26% | 460 | 35 | 29.5 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 10 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT2 | closed-circuit | 1 | 10000000 | W | 3.15% | 460 | 39 | 32 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | O&M_% | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT2 | closed-circuit | 10000000 | 10000000000000000 | W | 3.15% | 460 | 39 | 32 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)

## heat_sink
Description | code | type | cap_min | cap_max | unit | aux_power | V_power_supply | T_water_in_design | T_water_out_design | T_water_in_sink | Water_source_code | medium_in | medium_out | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
Lake-water HEX | HEXLW | counter-flow, plate | 1 | 10000000000 | W | 1.1% | 460 | 35 | 29.5 | 27 | LW | water | water | USD-2015 | 1000 | 0.0001 | 1 | 0 | 0 | 20 | 5 | 1 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
Sewage-water HEX | HEXSW | counter-flow, plate | 1 | 10000000000 | W | 1.1% | 460 | 35 | 29.5 | 35 | SW | water | water | USD-2015 | 1000 | 0.0001 | 1 | 0 | 0 | 20 | 5 | 1 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
Groundwater-water HEX | HEXGW | counter-flow, plate | 1 | 10000000000 | W | 1.1% | 460 | 35 | 29.5 | 27 | GW | water | water | USD-2015 | 1000 | 0.0001 | 1 | 0 | 0 | 20 | 5 | 1 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications

## heat_pumps
Description | code | type | cap_min | cap_max | unit | min_eff_rating_seasonal | V_power_supply | T_evap_design | T_cond_design | medium_evap_side | medium_cond_side | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
geothermal heat pump - closed loop | HP1 | geothermal | 0 | 40000 | W | 3.1 | 380 | 0 | 27 | brine | air | USD-2015 | 0 | 197.1175 | 0.49 | 0 | 0 | 20 | 1 | 5 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
geothermal heat pump - closed loop | HP1 | geothermal | 40000 | 100000000 | W | 2.8 | 380 | 0 | 27 | brine | air | USD-2015 | 0 | 197.1175 | 0.49 | 0 | 0 | 20 | 1 | 5 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
water-source heat pump | HP2 | water-source | 0 | 21000 | W | 4.3 | 380 | 20 | 27 | water | air | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
water-source heat pump | HP2 | water-source | 21000 | 40000 | W | 4.3 | 380 | 20 | 27 | water | air | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
water-source heat pump | HP2 | water-source | 40000 | 75000 | W | 4 | 380 | 20 | 27 | water | air | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
water-source heat pump | HP2 | water-source | 75000 | 20000000 | W | 3.9 | 380 | 20 | 27 | water | air | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 |  | ASHRAE 90.1/2019 - AHRI 1230/2021
air-water heat pump | HP3 | air-source | 0 | 21000 | W | 2.2 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 7.7 | 1 | 0 | 0 | 25 | 5 | 6 | cost | ASHRAE 90.1/2019 - AHRI 210.240/2023
air-water heat pump | HP3 | air-source | 21000 | 40000 | W | 3.3 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 7.7 | 1 | 0 | 0 | 25 | 5 | 6 | cost | ASHRAE 90.1/2019 - AHRI 210.240/2023
air-water heat pump | HP3 | air-source | 40000 | 75000 | W | 3.3 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 7.7 | 1 | 0 | 0 | 25 | 5 | 6 | cost | ASHRAE 90.1/2019 - AHRI 210.240/2023
air-water heat pump | HP3 | air-source | 75000 | 10000000 | W | 3.2 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 7.7 | 1 | 0 | 0 | 25 | 5 | 6 | cost | ASHRAE 90.1/2019 - AHRI 210.240/2023

## boilers
Description | code | type | fuel_code | cap_min | cap_max | unit | min_eff_rating | T_water_in_rating | T_water_out_rating | T_flue_gas_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
conventional natural gas boiler | BO1 | gas | Cgas | 1 | 90000 | W | 82% | 26.5 | 82 | 126 | USD-2015 | 22505.5432 | 0.30488 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
conventional natural gas boiler | BO1 | gas | Cgas | 90000 | 730000 | W | 80% | 26.5 | 82 | 126 | USD-2015 | 38913.5255 | 0.12195 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
conventional natural gas boiler | BO1 | gas | Cgas | 730000 | 10000000000 | W | 82% | 26.5 | 82 | 126 | USD-2015 | 93126.3858 | 0.015521 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
conventional oil boiler | BO2 | oil | Coil | 1 | 90000 | W | 84% | 26.5 | 82 | 126 | USD-2015 | 22505.5432 | 0.30488 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
conventional oil boiler | BO2 | oil | Coil | 90000 | 730000 | W | 82% | 26.5 | 82 | 126 | USD-2015 | 38913.5255 | 0.12195 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
conventional oil boiler | BO2 | oil | Coil | 730000 | 10000000000 | W | 84% | 26.5 | 82 | 126 | USD-2015 | 93126.3858 | 0.015521 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
condensing natural gas boiler | BO3 | gas-cond | Cgas | 1 | 90000 | W | 92% | 26.5 | 82 | 88 | USD-2015 | 22505.5432 | 0.30488 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
condensing natural gas boiler | BO3 | gas-cond | Cgas | 90000 | 730000 | W | 90% | 26.5 | 82 | 88 | USD-2015 | 38913.5255 | 0.12195 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures
condensing natural gas boiler | BO3 | gas-cond | Cgas | 730000 | 10000000000 | W | 92% | 26.5 | 82 | 88 | USD-2015 | 93126.3858 | 0.015521 | 1 | 0 | 0 | 20 | 5 | 5 |  | ASHRAE 90.1/2019 - minimum efficiency rating, 10 CFR Appendix A - boiler testing temperatures

## cogeneration_plants
Description | code | type | fuel_code | cap_min | cap_max | unit | elec_eff_design | therm_eff_design | V_power_out_design | T_water_out_design | T_flue_gas_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 850000 | 2600000 | W | 40% | 47% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 2600000 | 3500000 | W | 43% | 44% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 3500000 | 10000000 | W | 45.5% | 43% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 180000 | 280000 | W | 35% | 39% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 280000 | 900000 | W | 39% | 40% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 900000 | 2600000 | W | 42% | 41% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biomass furnace combined with ORC | FORC1 | furnace | Cwbm | 1000000 | 5000000 | W | 15% | 65% | 380 | 100 | 250 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
biomass furnace combined with ORC | FORC1 | furnace | Cwbm | 5000000 | 50000000 | W | 17% | 67% | 380 | 100 | 250 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
oil furnace combined with ORC | FORC1 | furnace | Cwbm | 1000000 | 50000000 | W | 18% | 80% | 380 | 100 | 350 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
combined cycle gas turbine with heat recovery | CCGT1 | turbine | Cgas | 30000000 | 150000000 | W | 62% | 29% | 380 | 100 | 150 | USD-2015 | 0 | 555.8316 | 0.5967 | 0 | 0 | 25 | 3 | 6 | all | Mitsubishi Gas Trubine Combined Cycle Catalogue 2022

## thermal_energy_storages
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | LT_mat_yr | O&M_% | IR_% | C_mat_% | T_PHCH_C | T_min_C | T_max_C | HL_kJkg | Rho_T_PHCH_kgm3 | Cp_kJkgK | n_ch | n_disch | assumption
long-term storage tank | TES1 | HEATING | 100 | 12000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 25 | 1 | 6 | 0 | 0 | 70 | 90 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
long-term storage tank | TES1 | HEATING | 12000 | 10000000000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 25 | 1 | 6 | 0 | 0 | 70 | 90 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_max
short-term storage tank - water | TES2 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 108 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 0 | 0 | 4 | 13 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank- ice | TES3 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 4.8 | 0 | -0.5 | 0.5 | 334 | 917 | 2.11 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - eutectic salt | TES4 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 4.8 | 4 | 3.5 | 4.5 | 234 | 1600 | 2 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - PEG400 | TES5 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 156.3 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 27.3 | 5.4 | 4.9 | 5.9 | 105 | 1125 | 2.09 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - Paraffin C14 | TES6 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 141.5 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 19.7 | 5 | 4.5 | 5.5 | 230 | 760 | 2.14 | 0.98 | 0.96 | cap_min, cap_max

## heat_exchangers
Description | code | type | cap_min | cap_max | unit | T_min_operating | T_max_operating | medium_in | medium_out | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
substation heat exchanger | HEX1 | counter-flow, plate | 1 | 80000 | W | -20 | 160 | water | water | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
substation heat exchanger | HEX1 | counter-flow, plate | 80000 | 100000 | W | -20 | 160 | water | water | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
substation heat exchanger | HEX1 | counter-flow, plate | 100000 | 10000000000 | W | -20 | 160 | water | water | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications

## power_transformers
Description | code | type | cap_min | cap_max | unit | V_min_lowV_side | V_max_lowV_side | V_min_highV_side | V_max_highV_side | current_form_lowV | current_form_highV | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
small power transformer | TR1 | small interconnection transformer | 0 | 25000 | VA | 1 | 360 | 360 | 1100 | AC | AC | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017
medium power transformer | TR2 | medium interconnection transformer | 5000 | 40000000 | VA | 1 | 1100 | 1100 | 36000 | AC | AC | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017
large power transformer | TR3 | large interconnection transformer | 5000 | 100000000 | VA | 1 | 36000 | 36000 | 100000 | AC | AC | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017

## inverters
Description | code | type | cap_min | cap_max | unit | V_min_lowV_side | V_max_lowV_side | V_min_highV_side | V_max_highV_side | current_form_lowV | current_form_highV | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
inverter | IN1 | inverter | 0 | 100000000 | VA | 1 | 1500 | 1 | 1500 | DC | AC | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017

## hydraulic_pumps
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic pump | PU1 | 500 | 4000 | W | USD-2015 | 0 | 29.3139 | 0.5216 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 4000 | 37000 | W | USD-2015 | 0 | 4.323 | 0.7464 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 375000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 10000000000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | all

## bore_holes
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
borehole | BH1 | 1 | 10000000000 | W | USD-2015 | 0 | 47.4279 | 0.74 | 0 | 0 | 50 | 0 | 5