## HEATING
Description | code | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
None | SUPPLY_HEATING_AS0 | NONE | NONE | 0 | 0 | 20 | 1 | 1.3 | educated guess

## HOT_WATER
Description | code | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
None | SUPPLY_HOTWATER_AS0 | NONE | NONE | 0 | 0 | 20 | 1 | 1.3 | educated guess
Electrical boiler | SUPPLY_HOTWATER_AS1 | GRID | BUILDING | 0.9 | 200 | 20 | 5 | 1.3 | educated guess
Note on A3: Jimeno Fonseca: All values + 15% of vertailverluste not included in th original factors. In order to trasnform from useful to final energy

## COOLING
Description | code | system | feedstock | scale | efficiency | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
None | SUPPLY_COOLING_AS0 | NONE | NONE | NONE | 0 | 0 | 20 | 1 | 3 | interest_rate = maximum 2 right now (https://www.visualcapitalist.com/chart-the-downward-spiral-in-interest-rates/) / Natalia Borzino: 3% discoutn rate (natalia.borzino@frs.ethz.ch)
Vapor compression chiller and dry cooling tower (building scale) | SUPPLY_COOLING_AS1 | COOLING | GRID | BUILDING | 2.7458 | 710 | 20 | 3 | 3 | efficiency: " BCA: Listing of Building Energy Performance Data for 2018 averaged 'Centralised Air-conditioning Plant Efficiency (kW/RT)' values of all benchmarked Air Cooled Chilled Water Plant" O&m_%: "Quatar: District Cooling Service - Presentation to Qatar Rail https://de.slideshare.net/JaygopalKottilil/district-cooling-service-presentation-to-qatar-rail-47232121"
Vapor compression chiller and wet cooling tower (building scale) | SUPPLY_COOLING_AS2 | COOLING | GRID | BUILDING | 3.88 | 852 | 20 | 4 | 3 | efficiency: "Statistical Analysis of VCC+CT simulations using CEAs decentralized optimization script, with the consideration of partial loads"; CAPEX_USD2015: "Construction Cost Handbook Singapore 2016 (Arcadis) "
Vapor compression chiller and sea water heat exchanger (district scale) | SUPPLY_COOLING_AS3 | COOLING | GRID | DISTRICT | 6.5 | 1944 | 50 | 2.5 | 3 | efficiency: "Choosing heat sinks for cooling in tropical climates. Bruelisauer et al. (2013)" CAPEX_USD2015: "FINAL FEASIBILITY REPORT Male’ and Hulhumale´ District Cooling Feasibility Study, devcco, ASHRAE District Cooling Guide 2013, Construction Cost Handbook Singapore 2016 (Arcadis) "
Vapor compression chiller and wet cooling tower (district scale) | SUPPLY_COOLING_AS4 | COOLING | GRID | DISTRICT | 4.64 | 1514 | 50 | 2 | 3 | efficiency: "Statistical Analysis of VCC+CT district cooling plant using CEAs centralized optimization script, with the consideration of partial loads" CAPEX_USD2015: "ASHRAE District Cooling Guide 2013, Construction Cost Handbook Singapore 2016 (Arcadis) "
Direct Expansion Unit (building scale) | SUPPLY_COOLING_AS5 | COOLING | GRID | BUILDING | 2.3 | 271 | 15 | 12 | 3 | efficiency: "Stuck-effect Units from: Stuck in a stack—Temperature measurements of the microclimate around split type condensing units in a high rise building in Singapore. Marcel Bruelisauer et al" CAPEX_USD2015kW: "https://www.lazada.sg/products/mitsubishi-starmex-inverter-system-3-air-conditioner-with-installation-i321630204-s640522722.html?spm=a2o42.searchlist.list.13.64e653b6LB0WXz&search=1"

## ELECTRICITY
Description | code | feedstock1 | scale1 | efficiency1 | feedstock2 | scale2 | aarea_pv | CAPEX_USD2015kW | LT_yr | O&M_% | IR_% | reference
None | SUPPLY_ELECTRICITY_AS0 | NONE | NONE | 0 | NONE | NONE | 0 | 0 | 20 | 1.3 | 1.3 | educated guess
Singaporean consumer mix | SUPPLY_ELECTRICITY_AS1 | GRID | CITY | 0.99 | NONE | NONE | 0 | 62.1 | 20 | 1.3 | 1.3 | CAPEX_USD2015: Industry Source for E/I&C investment costs
Singaporean consumer mix 90% + 20m2 PV onsite | SUPPLY_ELECTRICITY_AS2 | GRID | CITY | 0.95 | SOLAR | BUILDING | 20 | 0 | 20 | 1.3 | 1.3 | educated guess