## PHOTOVOLTAIC_PANELS
Description | code | type | cap_min | cap_max | unit | module_length_m | PV_th | PV_n | PV_noct | PV_Bref | PV_a0 | PV_a1 | PV_a2 | PV_a3 | PV_a4 | misc_losses | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | capacity_Wp | module_area_m2 | primary_energy_kWh_m2 | cost_facade_euro_m2 | cost_roof_euro_m2 | module_embodied_kgco2m2 | source
typical csi 2024 (BIPV) | PV1 | PV | 1 | 10000000000 | W | 1 | 0.002 | 0.18464 | 45.1 | 0.00381 | 0.9191 | 0.09988 | -0.04273 | 0.00937 | -0.000764 | 0.1 | USD-2015 | 0 | 2.6 | 1 | 0 | 0 | 25 | 1 | 5 | IR_% | 325.7037 | 1.76 | 831.8 | 345.72 | 254.72 | 255.7662 | jmccarty CACTUS
typical mcsi 2024 (BIPV) | PV2 | PV | 1 | 10000000000 | W | 1 | 0.002 | 0.17503 | 45.2 | 0.00409 | 0.92194 | 0.070892 | -0.014272 | 0.001171 | -3.4e-05 | 0.1 | USD-2015 | 0 | 2.6 | 1 | 0 | 0 | 25 | 1 | 5 | IR_% | 335.1598 | 1.91 | 631.7 | 329.58 | 238.58 | 191.1831 | jmccarty CACTUS
typical cdte 2024 (BIPV) | PV3 | PV | 1 | 10000000000 | W | 1 | 0.002 | 0.176 | 50.7 | 0.00307 | 0.9196 | 0.07164 | -0.01338 | 0.000961 | -2.5e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 25 | 1 | 5 | IR_% | 430.936 | 2.45 | 153.1 | 330.54 | 239.54 | 47.5504 | jmccarty CACTUS
typical cigs 2024 (BIPV) | PV4 | PV | 1 | 10000000000 | W | 1 | 0.002 | 0.099396 | 55.7 | 0.00385 | 0.9354 | 0.06809 | -0.02094 | 0.00293 | -0.000156 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 25 | 1 | 5 | IR_% | 164.9981 | 1.66 | 246 | 356.06 | 265.06 | 75.9144 | jmccarty CACTUS

## SOLAR_THERMAL_PANELS
Description | code | type | module_length_m | module_area_m2 | aperture_area_ratio | n0 | c1 | c2 | mB0_r | mB_max_r | mB_min_r | C_eff | t_max | IAM_d | dP1 | dP2 | dP3 | dP4 | Cp_fluid | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
flat plate | SC1 | FP | 2 | 2.023 | 0.888 | 0.775 | 3.91 | 0.0081 | 57.98 | 86.97 | 28.99 | 8000 | 192 | 0.87 | 0 | 94.6324 | 150.2986 | 44.5329 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%
evacuated tube | SC2 | ET | 2 | 4.322 | 0.655 | 0.721 | 0.89 | 0.0199 | 88.2 | 147.12 | 33.1 | 39000 | 196 | 0.91 | 0 | 2825.9464 | 7771.3527 | 706.4866 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%

## PHOTOVOLTAIC_THERMAL_PANELS
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic PVT | PVT1 | 1 | 10000000000 | W | USD-2015 | 0 | 5.1975 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%

## BOILERS
Description | code | type | fuel_code | cap_min | cap_max | unit | min_eff_rating | T_water_in_rating | T_water_out_rating | T_flue_gas_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
conventional natural gas boiler | BO1 | gas | Cgas | 1 | 20000 | W | 93% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.22109 | 1 | 0 | 0 | 20 | 5 | 5 | Assumed equal to condensing boiler
conventional natural gas boiler | BO1 | gas | Cgas | 20000 | 30000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.12755 | 1 | 0 | 0 | 20 | 5 | 5 | Assumed equal to condensing boiler
conventional natural gas boiler | BO1 | gas | Cgas | 30000 | 60000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.11054 | 1 | 0 | 0 | 20 | 5 | 5 | Assumed equal to condensing boiler
conventional natural gas boiler | BO1 | gas | Cgas | 60000 | 10000000000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.10629 | 1 | 0 | 0 | 20 | 5 | 5 | Assumed equal to condensing boiler
conventional oil boiler | BO2 | oil | Coil | 1 | 20000 | W | 92% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.66837 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2015 | KEA Badenwürttemberg Technikkatalog
conventional oil boiler | BO2 | oil | Coil | 20000 | 30000 | W | 93% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.44218 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2016 | KEA Badenwürttemberg Technikkatalog
conventional oil boiler | BO2 | oil | Coil | 30000 | 60000 | W | 93% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.34184 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2017 | KEA Badenwürttemberg Technikkatalog
conventional oil boiler | BO2 | oil | Coil | 60000 | 10000000000 | W | 93% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.15901 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2017 | KEA Badenwürttemberg Technikkatalog
condensing natural gas boiler | BO3 | gas | Cgas | 1 | 20000 | W | 93% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.22109 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2015 | KEA Badenwürttemberg Technikkatalog
condensing natural gas boiler | BO3 | gas | Cgas | 20000 | 30000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.12755 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2016 | KEA Badenwürttemberg Technikkatalog
condensing natural gas boiler | BO3 | gas | Cgas | 30000 | 60000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.11054 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2017 | KEA Badenwürttemberg Technikkatalog
condensing natural gas boiler | BO3 | gas | Cgas | 60000 | 10000000000 | W | 95% | 26.5 | 82 | 126 | USD-2015 | 0 | 0.10629 | 1 | 0 | 0 | 20 | 5 | 5 | 1,176 EUR 2022 = 1 USD 2017 | KEA Badenwürttemberg Technikkatalog
electrical boiler | BO5 | electricity | E230AC | 1 | 10000000000 | W | 1 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.29082 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2017 | KEA Badenwürttemberg Technikkatalog
wood-furnace | BO6 | wood | Cwod | 1 | 30000 | W | 0.94 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.94813 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2020 | KEA Badenwürttemberg Technikkatalog
wood-furnace | BO6 | wood | Cwod | 30000 | 60000 | W | 0.94 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.45323 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2021 | KEA Badenwürttemberg Technikkatalog
wood-furnace | BO6 | wood | Cwod | 60000 | 230000 | W | 0.94 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.19898 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2022 | KEA Badenwürttemberg Technikkatalog
biomass pellet boiler | BO7 | biomass | Cdbm | 1 | 20000 | W | 0.9 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.63265 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2023 | KEA Badenwürttemberg Technikkatalog
biomass pellet boiler | BO7 | biomass | Cdbm | 20000 | 60000 | W | 0.85 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.34439 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2024 | KEA Badenwürttemberg Technikkatalog
biomass pellet boiler | BO7 | biomass | Cdbm | 60000 | 1000000000 | W | 0.81 | 26.5 | 82 | 126 | USD-2015 | 0 | 0.2585 | 1 | 0 | 0 | 20 | 6 | 5 | 1,176 EUR 2022 = 1 USD 2025 | KEA Badenwürttemberg Technikkatalog

## COGENERATION_PLANTS
Description | code | type | fuel_code | cap_min | cap_max | unit | elec_eff_design | therm_eff_design | V_power_out_design | T_water_out_design | T_flue_gas_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 850000 | 2600000 | W | 40% | 47% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 2600000 | 3500000 | W | 43% | 44% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
natural powered otto engine with heat recovery | OEHR1 | engine | Cgas | 3500000 | 10000000 | W | 45.5% | 43% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 2 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 180000 | 280000 | W | 35% | 39% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 280000 | 900000 | W | 39% | 40% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biogas powered otto engine with heat recovery | OEHR2 | bio-engine | Cbig | 900000 | 2600000 | W | 42% | 41% | 380 | 100 | 140 | USD-2015 | 0 | 1.81 | 1 | 0 | 0 | 30 | 3 | 5 | temperatures and cost | grouppo AB Ecomax catalogue 2022, US EIA Capital Cost for Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies 2020
biomass furnace combined with ORC | FU1 | furnace | Cwbm | 1000000 | 5000000 | W | 15% | 65% | 380 | 100 | 250 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
biomass furnace combined with ORC | FU1 | furnace | Cwbm | 5000000 | 50000000 | W | 17% | 67% | 380 | 100 | 250 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
oil furnace combined with ORC | FU2 | furnace | Cwbm | 1000000 | 50000000 | W | 18% | 80% | 380 | 100 | 350 | USD-2015 | 0 | 0.743 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://doi.org/10.1016/B978-0-08-100510-1.00015-6
combined cycle gas turbine with heat recovery | CCGT1 | turbine | Cgas | 30000000 | 150000000 | W | 62% | 29% | 380 | 100 | 150 | USD-2015 | 0 | 555.8316 | 0.5967 | 0 | 0 | 25 | 3 | 6 | all | Mitsubishi Gas Trubine Combined Cycle Catalogue 2022

## HEAT_EXCHANGERS
Description | code | type | cap_min | cap_max | unit | T_min_operating | T_max_operating | medium_in | medium_out | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
substation heat exchanger | HEX1 | counter-flow, plate | 1 | 80000 | W | -20 | 160 | water | water | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
substation heat exchanger | HEX1 | counter-flow, plate | 80000 | 100000 | W | -20 | 160 | water | water | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
substation heat exchanger | HEX1 | counter-flow, plate | 100000 | 10000000000 | W | -20 | 160 | water | water | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 20 | 5 | 5 | all | https://www.linquip.com/blog/efficiency-of-heat-exchanger/; Danfoss - Ultra efficient braze heat exhangers for your district energy applications
District substation heat exchanger | HEX2 | - | 0 | 500 | m^2 |  |  |  |  | USD-2015 | 3381 | 229.8 | 0 | 0 | 0 | 20 | 5 | 5 | Values under 1 and above 50 are assumptions, as no datasheet values are available in this area. a_p to e_p denote the pressure drop in Pa

## VAPOR_COMPRESSION_CHILLERS
Description | code | G_VALUE | type | cap_min | cap_max | unit | min_eff_rating | V_power_supply | T_cond_design | T_evap_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
electrically operated centrifugal, water cooled | CH1 | 0.47 | water-centrifugal | 1050000 | 70000000 | W | 6.3 | 380 | 34.61 | 6.67 | USD-2015 | 1568000 | 0.3049 | 1 | 0 | 0 | 25 | 5 | 5 | Fit based on RESCUE WP 2.4. Figure 18 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | 0.4 | water-reciprocating | 1 | 260000 | W | 4.7 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | 0.4 | water-reciprocating | 260000 | 530000 | W | 4.9 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | 0.4 | water-reciprocating | 530000 | 1050000 | W | 5.3 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | 0.4 | water-reciprocating | 1050000 | 2110000 | W | 5.8 | 380 | 34.61 | 6.67 | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load
electrically operated positive displacement, water cooled | CH2 | 0.4 | water-reciprocating | 2110000 | 70000000 | W | 6.3 | 380 | 34.61 | 6.67 | USD-2015 | 0 | 0.36063 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | ASHRAE 90.1/2019 - minimum efficiency rating at full load

## ABSORPTION_CHILLERS
Description | code | type | cap_min | cap_max | unit | min_eff_rating | aux_power | V_power_supply | T_gen_design | T_cond_design | T_evap_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | s_e | r_e | s_g | r_g | a_e | e_e | a_g | e_g | m_cw | m_hw | reference
LiBr single effect - indirect | ACH1 | single | 0 | 51150 | W | 0.7 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 3.23 | 2.14 | ASHRAE 90.1/2019 - minimum efficiency rating at full load; https://www.esmagazine.com/articles/82307-basics-for-absorption-chillers - capacity-specific mass-flow rates
LiBr single effect - indirect | ACH1 | single | 51150 | 1176000 | W | 0.7 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 68.12 | -3281.1 | 88.05 | -4216.1 | -1.45 | 1.75 | -1.45 | 1.75 | 81 | 33 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr double effect (dummy) - indirect | ACH2 | double | 0 | 58150 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 3.74 | 2.5 | ASHRAE 90.1/2019 - minimum efficiency rating at full load; https://www.esmagazine.com/articles/82307-basics-for-absorption-chillers - capacity-specific mass-flow rates
LiBr double effect - indirect | ACH2 | double | 58150 | 1337450 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14 | ASHRAE 90.1/2019 - minimum efficiency rating at full load
LiBr double effect - indirect | ACH2 | double | 1337450 | 10000000000 | W | 1 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 646 | 431 | ASHRAE 90.1/2019 - minimum efficiency rating at full load; https://www.esmagazine.com/articles/82307-basics-for-absorption-chillers - capacity-specific mass-flow rates
LiBr triple effect - indirect | ACH3 | triple | 116300 | 1628200 | W | 1.2 | 0.01 | 460 | 90 | 38 | 7 | USD-2015 | 0 | 0.6424 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 14.6 | -1171.7 | 7.05 | -504.2 | -2.14 | 3.29 | -2.14 | 3.29 | 62 | 10

## COOLING_TOWERS
Description | code | type | cap_min | cap_max | unit | aux_power | V_power_supply | T_water_in_design | T_water_out_design | T_air_in_design | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
centralized cooling tower | CT1 | open-circuit | 1 | 10000000 | W | 1.26% | 460 | 35 | 29.5 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 10 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT1 | open-circuit | 10000000 | 10000000000000000 | W | 1.26% | 460 | 35 | 29.5 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 10 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT2 | closed-circuit | 1 | 10000000 | W | 3.15% | 460 | 39 | 32 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | O&M_% | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)
centralized cooling tower | CT2 | closed-circuit | 10000000 | 10000000000000000 | W | 3.15% | 460 | 39 | 32 | 24 | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | all | ASHRAE 90.1/2019 - auxilary power demand (i.e. performance requirement, converted)

## FUEL_CELLS
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | Assumptions
solid oxide fuel cell | FC1 | 1000 | 10000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5
solid oxide fuel cell | FC1 | 1 | 10000000000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5 | everything

## UNITARY_AIR_CONDITIONERS
Description | code | type | cap_min | cap_max | unit | rated_COP_seasonal | V_power_supply | T_air_indoor_rating | T_air_outdoor_rating | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
air conditioner, split-system, air cooled | AC1 | mini-split | 0 | 19000 | W | 3.7 | 230 | 27 | 35 | USD-2015 | 0 | 1.6 | 1 | 0 | 0 | 25 | 5 | 5 | all | ASHRAE 90.1/2019 - minimum efficiency rating, AHRI 210/240 (2023) temperature rating - application rating conditions
air conditioner, split-system, air cooled, ducted | AC2 | mini-split, ducted | 0 | 19000 | W | 3.5 | 230 | 27 | 35 | USD-2015 | 0 | 1.6 | 1 | 0 | 0 | 25 | 5 | 5 | all | ASHRAE 90.1/2019 - minimum efficiency rating, AHRI 210/240 (2023) temperature rating - application rating conditions

## HEAT_PUMPS
Description | code | type | cap_min | cap_max | unit | min_eff_rating_seasonal | V_power_supply | T_evap_design | T_cond_design | medium_evap_side | medium_cond_side | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
geothermal heat pump - closed loop | HP1 | geothermal | 0 | 40000 | W | 4.3 | 380 | 0 | 27 | brine | air | USD-2015 | 0 | 0.99915 | 1 | 0 | 0 | 20 | 1 | 5 |  | KEA badenwürttemberg
geothermal heat pump - closed loop | HP1 | geothermal | 40000 | 100000000 | W | 4.3 | 380 | 0 | 27 | brine | air | USD-2015 | 0 | 0.54932 | 1 | 0 | 0 | 20 | 1 | 5 |  | KEA badenwürttemberg
water-source heat pump | HP2 | water-source | 0 | 20000 | W | 4.9 | 380 | 20 | 27 | water | water | USD-2015 | 0 | 0.86224 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
water-source heat pump | HP2 | water-source | 20000 | 40000 | W | 4.9 | 380 | 20 | 27 | water | water | USD-2015 | 0 | 0.57398 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
water-source heat pump | HP2 | water-source | 40000 | 60000 | W | 4.9 | 380 | 20 | 27 | water | water | USD-2015 | 0 | 0.45493 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
water-source heat pump | HP2 | water-source | 60000 | 20000000 | W | 4.9 | 380 | 20 | 27 | water | water | USD-2015 | 0 | 0.32398 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
air-water heat pump | HP3 | air-source | 0 | 20000 | W | 3.4 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 1.0714 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
air-water heat pump | HP3 | air-source | 20000 | 40000 | W | 3.3 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 0.92772 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
air-water heat pump | HP3 | air-source | 40000 | 60000 | W | 3.3 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 0.85374 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg
air-water heat pump | HP3 | air-source | 60000 | 10000000 | W | 3.2 | 230 | 7 | 35 | air | water | USD-2015 | 0 | 0.75255 | 1 | 0 | 0 | 25 | 5 | 6 |  | KEA badenwürttemberg

## THERMAL_ENERGY_STORAGES
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | LT_mat_yr | O&M_% | IR_% | C_mat_% | T_PHCH_C | T_min_C | T_max_C | HL_kJkg | Rho_T_PHCH_kgm3 | Cp_kJkgK | n_ch | n_disch | assumption
long-term storage tank | TES1 | HEATING | 100 | 12000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 25 | 1 | 6 | 0 | 0 | 70 | 90 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
long-term storage tank | TES1 | HEATING | 12000 | 10000000000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 25 | 1 | 6 | 0 | 0 | 70 | 90 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_max
short-term storage tank - water | TES2 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 108 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 0 | 0 | 4 | 13 | 0 | 997 | 4.19 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank- ice | TES3 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 25 | 2 | 6 | 4.8 | 0 | -0.5 | 0.5 | 334 | 917 | 2.11 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - eutectic salt | TES4 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 117.9 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 4.8 | 4 | 3.5 | 4.5 | 234 | 1600 | 2 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - PEG400 | TES5 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 156.3 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 27.3 | 5.4 | 4.9 | 5.9 | 105 | 1125 | 2.09 | 0.98 | 0.96 | cap_min, cap_max
short-term storage tank - Paraffin C14 | TES6 | COOLING | 0 | 10000000000 | kWh | USD-2015 | 0 | 141.5 | 1 | 0 | 0 | 25 | 7 | 2 | 6 | 19.7 | 5 | 4.5 | 5.5 | 230 | 760 | 2.14 | 0.98 | 0.96 | cap_min, cap_max

## POWER_TRANSFORMERS
Description | code | type | cap_min | cap_max | unit | V_min_lowV_side | V_max_lowV_side | V_min_highV_side | V_max_highV_side | current_form_lowV | current_form_highV | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | reference
small power transformer | TR1 | small interconnection transformer | 0 | 25000 | VA | 1 | 360 | 360 | 1100 | AC | AC | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017
medium power transformer | TR2 | medium interconnection transformer | 5000 | 40000000 | VA | 1 | 1100 | 1100 | 36000 | AC | AC | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017
large power transformer | TR3 | large interconnection transformer | 5000 | 100000000 | VA | 1 | 36000 | 36000 | 100000 | AC | AC | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 20 | 5 | 5 | cost | EN 50588-1, 2017

## HYDRAULIC_PUMPS
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic pump | PU1 | 500 | 4000 | W | USD-2015 | 0 | 29.3139 | 0.5216 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 4000 | 37000 | W | USD-2015 | 0 | 4.323 | 0.7464 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 375000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 10000000000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | all

## BORE_HOLES
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
borehole | BH1 | 1 | 10000000000 | W | USD-2015 | 0 | 47.4279 | 0.74 | 0 | 0 | 50 | 0 | 5